## MM102LMOD
Table Modbus
MM102LMOD : Compteur électrique modulaire monophasé 100 A RS485 Modbus simple tarif affichage LCD Certifié MID
Paramètre par défaut
Baud : |  | 9600
Adresse Modbus en décimal : |  | 3 dernier chiffres du numéro de série
Parité : |  | EVEN
Stop Bit : |  | 1
Data Bit : |  | 8
1：Instantaneous parameters
Modbus register address | R/W | Register length | Data Description | Unit | Content | Remark
0100 | R | 2 | INT32(3+3) | V | voltage
0102 | R | 2 | INT32(2+3) | A | current | forward and reverse(modbus)
0104 | R | 2 | INT32(5+0) | W | active power | forward and reverse(modbus)
0106 | R | 2 | INT32(5+0) | VA | apparent power
0108 | R | 2 | INT32(5+0) | var | reactive power | forward and reverse(modbus)
010A | R | 1 | INT16(2+1) | Hz | frequency
010B | R | 1 | INT16(1+3) | PF | power factor | With CL indication, active power with sign of forward and reverse(modbus)
2：Energy parameters
Modbus register address | R/W | Register length | Data Description | Unit | Content | Remark
010E | R | 2 | INT32(6+2) | kWh | Total forward active energy
0118 | R | 2 | INT32(6+2) | kWh | Total reverse active energy
0122 | R | 2 | INT32(6+2) | kWh | Total active energy | You can choose (forward), (reverse), (forward+reverse), (forward-reverse) by the synthetic code
012C | R | 2 | INT32(6+2) | kvarh | Total forward reactive energy
0136 | R | 2 | INT32(6+2) | kvarh | Total reverse reactive energy
0140 | R | 2 | INT32(6+2) | kvarh | Total reactive energy | You can choose (forward), (reverse), (forward+reverse), (forward-reverse) by the synthetic code
014A | R | 2 | INT32(6+2) | kvarh | Total reactive energy in the first quadrant
0154 | R | 2 | INT32(6+2) | kvarh | Total reactive energy in the second quadrant
015E | R | 2 | INT32(6+2) | kvarh | Total reactive energyin the third quadrant
0168 | R | 2 | INT32(6+2) | kvarh | Total reactive energy in the fourth quadrant
0172 | R | 2 | INT32(6+2) | kWh | Resettable total active energy
0174 | R | 2 | INT32(6+2) | kvarh | Resettable total reactive energy
0176 | R | 2 | INT32(6+1) | W | forward active demand
0178 | R | 2 | INT32(6+1) | W | forward maximum active energy demand
017A | R | 2 | INT32(6+1) | W | reverse active demand
017C | R | 2 | INT32(6+1) | W | reverse maximum active energy demand
0180 | R | 2 | INT32(6+1) | var | forward reactive demand
0182 | R | 2 | INT32(6+1) | var | forward maximum reactive demand
0184 | R | 2 | INT32(6+1) | var | reverse reactive demand
0186 | R | 2 | INT32(6+1) | var | reverse maximum reactive demand
3：Meter parameters
Modbus register address | R/W | Register length | Data Description | Unit | Content | Remark
1000 | R.W | 6 | 12-bit serial number,the same as DLT645 ID,it need to use 10h together, hexadecimal , 012345678910H serial number is 012345678910 |  | Serial No.
1003 | R.W | 1 | 1-247 |  | Modbus ID
1004 | R | 1 | 101 |  | FW version
1005 | R | 1 | 101 |  | HW version
1006 | R | 1 | XXXX |  | FW Checksum
100B | R.W | 1 | 0-99 |  | Scrolling time
100C | R.W | 1 | 1=300 2=600 3=1200 4=2400 5=4800 6=9600 7=19200 8=38400 9=115200 (Actually only 9600, 19200, 38400, 115200 are supported) |  | 485 baud rate
100D | R.W | 1 | 0=None 1=Odd 2=even |  | 485 check digit
100E | R.W | 1 | 1=1bit 2=2bit |  | 485 stop bit
100F | R.W | 1 | 1=total=forward 2=total=reverse 3=total=forward+reverse 4=total=forward-reverse |  | combined code
1010 |  | 1 | 0=Interval 1=Slip |  | demand mode
1011 | R.W | 1 | The unit minute can be set from 1-30, the default is 15 minutes |  | demand cycle
1012 | R.W | 4 | In bitwise,0 means no display, and need use the 10 control code should to write at one time (8 bytes are used for three-phase, but only 4 bytes are used for single-phase) |  | Cycle display content automatically
1016 | R.W | 1 | Can be set to 0000-9999 |  | password setting of the LCD button display
101A | R.W | 2 | Unit mA(startup current by default, maximum current's 1.2 times) 10 control code is used to write data at one time |  | Timing current value
2002 | W | 1 | bit12-Resettable total active energy bit13-Resettable total reactive energy |  | Clear energy
2003 | W | 1 | 0xA5XX bit0=forward active maximum demand bit1=reverse active maximum demand bit2=forward active maximum demand bit3=forward active maximum demand |  | Clear maximum demand